DO31 MAA

Fire door testing: 						(1 page)

This record sheet records the six-monthly testing of fire doors in the Museum.

Test procedure:

- Follow the examination procedure described by the Fire Safety Department

at: https://www.em.admin.cam.ac.uk/system/files/firedoorchecksguidance_0.pdf

Address the issue as identified or, if necessary, report faults to EM Helpdesk at efhelpdesk@admin.cam.ac.uk, CC to dir21@cam.ac.uk.

| Date | Id | Location | Result | Initials |
| --- | --- | --- | --- | --- |
|  |  | Workshop |  | F.G. |
|  |  | Ground Floor: W.B. → Main Entrance, Archaeology Building |  | F.G. |
|  |  | Ground Floor: W.B. → MAA Entrance lobby |  | F.G. |
|  |  | Ground Floor: W.B. Lobby → MAA |  | F.G. |
|  |  | Ground Floor Traka room → Keyser corridor |  | F.G. |
|  |  | Ground Floor Corridor → Stairs lobby |  | F.G. |
|  |  | 1st Floor lobby → Babington corridor |  | F.G. |
|  |  | 2nd Floor Mezz. Conservation Laboratory |  | F.G. |
|  |  | 2nd Floor Mezz. Staff Space |  | F.G. |
|  |  | 3rd Floor Mezz. Plant Room |  | F.G. |
|  |  | 3rd Floor Mezz. Store cupboard |  | F.G. |
|  |  | Photo Archive |  | F.G. |

DO31 MAA

Electronic lock testing: 					                           (1 page)

To be completed: Monthly

This record sheet relates to the green boxes by doors with magnetic locks.

Test procedure:

Note: Testing must be conducted when the door is locked. If the door is unlocked automatically according to a schedule, conduct the testing outside the times when the door can be opened without a card.

Note: If an alarm sounds when the lock is tested, Chubb says that this is only a local sounder and will stop when the lock is reset.

1.⁠ ⁠Insert the twin prongs of the black plastic key into the underside/base of the green box and pull down to remove it: The box will split in two, and the lower part will descend by perhaps 5 mm. Manually open the door to demonstrate that it is no longer controlled by the magnetic lock: It should open freely.

2.⁠ ⁠Reset the box by squeezing the two halves back together. Attempt to manually open the door to demonstrate that it is once again under the control of the magnetic lock

The requisite black testing keys may be obtained upon request from David Redhouse, within reason.

Report faults to EM Helpdesk efhelpdesk@admin.cam.ac.uk, CC to dir21@cam.ac.uk.

| Date | Id | Location | Result | Initials |
| --- | --- | --- | --- | --- |
|  |  | Keyser Storage |  | F.G. |
|  |  | Learning office |  | F.G. |
|  |  | Front of House office |  | F.G. |
|  |  | 1st Floor Gallery → Hall |  | F.G. |
|  |  | Babington Storage |  | F.G. |
|  |  | 2nd Floor Gallery → Hall |  | F.G. |
|  |  | Bevan Storage |  | F.G. |
|  |  | Photo Archive |  | F.G. |

DO31 MAA

Emergency lighting testing: 							(2 pages)

To be completed: Monthly

Test procedure: Use test key to operate testing mechanism. Check lighting units for green battery indicator. Report faults or red battery indicator to EM Helpdesk efhelpdesk@admin.cam.ac.uk, CC to dir21@cam.ac.uk.

| Date | Id | Location | Result | Initials |
| --- | --- | --- | --- | --- |
|  |  | G Outreach office, over door |  | F.G. |
|  |  | G Keyser office |  | F.G. |
|  |  | G Keyser workroom |  | F.G. |
|  |  | G Mezz Keyser store N |  | F.G. |
|  |  | G Mezz Keyser store S |  | F.G. |
|  |  | 1 Babington corridor N end |  | F.G. |
|  | E6B | 1 Babington store |  | F.G. |
|  | E11 | 1 Mezz Mezzanine store N end |  | F.G. |
|  | E9B | 2 East wall of lobby, near stairs to mezzanine |  | F.G. |
|  | E9A | 2 East side of door, inside Bevan Hall N end |  | F.G. |
|  |  | 2 West side of door, inside Bevan Store N end |  | F.G. |
|  | E8 | 2 Mezzanine W end of rack overlooking stairs |  | F.G. |
|  | E15 | 3 East side of door, inside N end of Store 1 |  | F.G. |
|  | E12 | 3 on pillar inside Store 2 |  | F.G. |

|  | E14 | 3 N side of door, inside photographic studio |  | F.G. |
| --- | --- | --- | --- | --- |
|  | E16 | 4 inside door of plant room |  | F.G. |
|  |  | Conservation laboratory landing Mezzanine |  | F.G. |
|  |  | Digital Suite |  | F.G. |
|  |  | Maudsley Gallery lighting by entrance |  | F.G. |
|  |  | Clarke Office |  | F.G. |
|  |  | Andrews Gallery by lift/entrance |  | F.G. |
|  |  | Outside Photographic Studio |  | F.G. |
|  |  | Bevan Workroom door to corridor |  | F.G. |
|  |  | Bevan Workroom entrance to Bevan Store |  | F.G. |

DO31 MAA

Final exit testing: 									(1 page)

To be completed: Monthly

This record sheet details fire escape routes and final exits in the Museum.

Test procedure:

1.⁠ ⁠Exit the building via the specified fire exit and walk to the fire assembly point in front of the McDonald Institute Courtyard Building.

2.⁠ ⁠Note fire hazards and obstructions along the way or at the end. For example:

a. Corridors used for storage

b. Locked doors

Address the issue as identified or, if necessary, report faults to the EM Helpdesk at efhelpdesk@admin.cam.ac.uk, CC to dir21@cam.ac.uk.

| Date | Id | Location | Result | Initials |
| --- | --- | --- | --- | --- |
|  |  | Front entrance |  | F.G. |
|  |  | Back door |  | F.G. |
|  |  | Room 304 trough West Building |  | F.G. |

Note locations and hazards below: