DO31 MAA

Electronic lock testing: 					                           (1 page)

To be completed: Monthly

This record sheet relates to the green boxes by doors with magnetic locks.

Test procedure:

Note: Testing must be conducted when the door is locked. If the door is unlocked automatically according to a schedule, conduct the testing outside the times when the door can be opened without a card.

Note: If an alarm sounds when the lock is tested, Chubb says that this is only a local sounder and will stop when the lock is reset.

1.⁠ ⁠Insert the twin prongs of the black plastic key into the underside/base of the green box and pull down to remove it: The box will split in two, and the lower part will descend by perhaps 5 mm. Manually open the door to demonstrate that it is no longer controlled by the magnetic lock: It should open freely.

2.⁠ ⁠Reset the box by squeezing the two halves back together. Attempt to manually open the door to demonstrate that it is once again under the control of the magnetic lock

The requisite black testing keys may be obtained upon request from David Redhouse, within reason.

Report faults to EM Helpdesk efhelpdesk@admin.cam.ac.uk, CC to dir21@cam.ac.uk.

| Date | Id | Location | Result | Initials |
| --- | --- | --- | --- | --- |
|  |  | Keyser Storage |  | F.G. |
|  |  | Learning office |  | F.G. |
|  |  | Front of House office |  | F.G. |
|  |  | 1st Floor Gallery → Hall |  | F.G. |
|  |  | Babington Storage |  | F.G. |
|  |  | 2nd Floor Gallery → Hall |  | F.G. |
|  |  | Bevan Storage |  | F.G. |
|  |  | Photo Archive |  | F.G. |